## ELECTRICAL-BOQ
ELECTRICAL, MCT, PROJECT, PUNE
Sr. No. | Description | Unit | 7F | 8F | Total | Rate |  | Amount
[5 empty] | Qty. | Supply | Installation | Supply | Installation
1 | LT PANELS AND SWITCH GEARS:
Providing and fixing of Panels as per technical specifications as per the power schematic diagram (SLD) or as described below.
Panels: To be CPRI approved.
Bus-bar rating to be refered from power schematic. Current density of Copper to be considered as 1.2 Amps and of Aluminium as 0.8 Amps per square inch respectively.
All Incomers/ Sub incomers to have Digital Load Manager with RS 485 port and all Incomer MCCBs' to have ON/OFF/TRIP indication
All Panels to be provided with ELR at all incomers. All MCCB's to be with S/C, O/C, E/F
All MCCBs' used in the UPS power distribution to be only thermal magnetic release and all MCBs' to be with curve 'D'
MCB compartment in all panels will be double door with acrylic door frame for visibility.
All UPS outgoing panels to have neutral current carrying capacity of 1.6 times the each phase.
1.1 | Main LT Panel -7F
Incomer:
1x 800A 4P, 50kA, MCCB
1x Load Manager (Dual monitoring for EB & DG both) with RS 485 port, 1 Sets of Indicating lamps R,Y,B with Control SP MCB, ON-OFF-TRIP indication and ELR to be considered at main incomer.
Busbar: Shall be Aluminium and of TPN configration. Current density to be considered 0.8 A / sq.mm
Outgoing:
5 Nos of 250A TPN MCCB. (3x 120kVA WS UPS, 1x Main LT Panel 8F, 1x Spare)
3 Nos of 100A TPN MCCB. (2x 40kVA Server UPS, 1x Spare)
2 Nos of 40A TPN MCCB. (1x 20kVA Emergency UPS, 1x Spare)
6 Nos of 63A FP MCB. (3x RPDB, 1x Automation DB, 2x Spare)
4 Nos of 40A FP MCB. (4x LDB)
8 stage 80kVAR Capacitor bank (2x 2.5, 1x 5, 2x 10, 2x 15, 1x 20), with reactors for harmonics filter
Sub-incomer for outgoing AC feeders:
1x 250A, FP, 36kA, MCCB
1x Load Manager with RS485, 1 Sets of Indicating lamps R,Y,B with Control SP MCB, ON-OFF-TRIP indication. Shunt trip of 230V AC, 50Hz to be provided.
Outgoings from sub-incomer:
6 Nos of 63A 4P MCB. (4x AHU, 2x Spare)
8 Nos of 40A 4P MCB. (3x UPS Room AC, 1x Board Room ODU, 2x Server Room, 2x Spare)
3 Nos of 40A DP MCB. (2x HUB Room AC, 1x Spare)
| Main LT Panel -7F | Each | 1 |  | 1
1.2 | Main LT Panel -8F
Incomer:
1x 250A 4P, 36kA, MCCB
1x Load Manager with RS485, 1 Sets of Indicating lamps R,Y,B with Control SP MCB, ON-OFF-TRIP indication and ELR to be considered at main incomer.
Busbar: Shall be Aluminium and of TPN configration. Current density to be considered 0.8 A / sq.mm
Outgoing:
6 Nos of 63A FP MCB. (3x RPDB, 1x Automation DB, 2x Spare)
4 Nos of 40A FP MCB. (4x LDB)
6 stage 40kVAR Capacitor bank (1x 2.5, 1x 7.5, 1x 5, 3x 10), with reactors for harmonics filter
Sub-incomer for outgoing AC feeders:
1x 200A, FP, 16kA, MCCB
1x Load Manager with RS485, 1 Sets of Indicating lamps R,Y,B with Control SP MCB, ON-OFF-TRIP indication. Shunt trip of 230V AC, 50Hz to be provided.
Outgoings from sub-incomer:
6 Nos of 63A 4P MCB. (4x AHU, 1x Recreation Area, 1x Spare)
6 Nos of 25A DP MCB. (2x HUB Room-1 AC, 2x HUB Room-2 AC, 2x Spare)
| Main LT Panel -8F | Each |  | 1 | 1
1.3 | Hot Standby UPS - 7F
Incomer:
1x 250A, TP+2N, 25kA, MCCB
1x Load Manager with RS485, 1 Sets of Indicating lamps R,Y,B with Control SP MCB.
Busbar: Shall be Cu. and of TP+2N configration.
Outgoing:
3 Nos of 200A TP+2N MCCB. (1x 120kVA WS UPS -7F, 1x 120kVA WS UPS -8F, 1x Spare)
2 Nos of 100A TP+2N MCCB. (1x 40kVA Server UPS -1, 1x 40kVA Server UPS -2)
| Hot Standby UPS - 7F | Each | 1 |  | 1
1.4 | Workstation UPS Output Panel-7F & 8F
Incomer:
1x 200A, TP+2N, 16kA, MCCB
1x Load Manager with RS485, 1 Sets of Indicating lamps R,Y,B with Control SP MCB.
Busbar: Shall be Cu. and of TP+2N configration.
Outgoing:
8 Nos of 63A TP+2N MCB. (5x UDB, 3x Spare)
| Workstation UPS Output Panel-7F & 8F | Each | 1 | 1 | 2
1.5 | Server UPS Output Panel
Incomer:
1x 63A, TP+2N, 16kA, MCCB
1x Load Manager with RS485, 1 Sets of Indicating lamps R,Y,B with Control MCB.
Busbar: Shall be Cu. and of TP+2N configration.
Outgoing:
6 Nos of 63A TPN MCB. (1x HUB DB-7F, 1x Server DB-7F, 2x HUB DB-8F, 2x Spare)
| Server UPS Output Panel | Each | 2 |  | 2
1.6 | MCCB in MS Enclosure - IP-43 protection. Indicating lamps to be provided.
1.6.1 | 630A, TPN MCCB, 50kA | Each |  |  | 0
1.6.2 | 200A, TPN MCCB, 16kA | Each | 1 | 0 | 1
1.6.3 | 125A, TPN MCCB, 16kA | Each |  |  | 0
1.6.4 | 63A, TPN MCCB, 16kA | Each |  |  | 0
TOTAL FOR LT PANELS AND SWITCH GEARS:
2 | LT CABLE.
Proving, Laying, Testing and Commissioing of 1.1kV grade, stranded aluminium / copper conductor, XLPE/ PVC insulated armoured/ unarmored, power / control cables. The cables shall be laid in tray / hume pipe / in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. The cost of tie and GI clamps/ supports/ fixing arrangements to be considered.
2.1 | XLPE Insulated Armoured Aluminium Conductor Cables
2.1.1 | 3.5C - 300 sq. mm AYFY | Mtrs | 345 | 0 | 345
2.1.2 | 3.5C - 185 sq. mm AYFY | Mtrs | 0 | 100 | 100
2.1.3 | 3.5C - 95 sq. mm AYFY | Mtrs | 0 | 0 | 0
2.1.4 | 4C - 50 sq. mm AYFY | Mtrs |  |  | 0
2.1.5 | 4C - 35 sq. mm AYFY | Mtrs |  |  | 0
2.1.6 | 4C - 25 sq. mm AYFY | Mtrs | 0 | 0 | 0
2.1.7 | 4C - 16 sq. mm | Mtrs | 1021 | 1031 | 2052
2.1.8 | 4C - 10 sq. mm | Mtrs | 241 | 241 | 482
2.2 | PVC FR Insulated & Un Armoured Copper flexible Conductor cables (YY Type)
2.2.1 | 1C - 95 sq. mm | Mtrs | 471 | 0 | 471
2.2.2 | 1C - 70 sq. mm | Mtrs |  |  | 0
2.2.3 | 1C - 35 sq. mm | Mtrs | 304 | 0 | 304
2.2.4 | 1C - 25 sq. mm | Mtrs |  |  | 0
2.2.5 | 1C - 16 sq. mm | Mtrs | 127 | 0 | 127
2.2.6 | 1C - 10 sq. mm | Mtrs |  |  | 0
2.3 | XLPE Insulated & Steel Armoured Copper Conductor cables (YFY Type)
2.3.1 | 4 Core - 120 Sq. mm YFY | Mtrs | 0 | 100 | 100
2.3.2 | 4 Core - 25 Sq. mm YFY | Mtrs |  |  | 0
2.3.3 | 4 Core - 16 Sq. mm YFY | Mtrs | 727 | 903 | 1630
2.3.4 | 4 Core - 10 Sq. mm YFY | Mtrs | 0 | 0 | 0
2.3.5 | 4 Core - 6 Sq. mm | Mtrs | 0 | 0 | 0
2.3.6 | 4 Core - 4 Sq. mm | Mtrs | 0 | 0 | 0
2.3.7 | 3 Core - 6 Sq. mm | Mtrs |  |  | 0
2.3.8 | 3 Core - 4 Sq. mm | Mtrs | 336 | 336 | 672
2.3.9 | 3 Core - 2.5 Sq. mm | Mtrs | 100 | 0 | 100
3 | END TERMINATIONS
Providing and Fixing of End terminations for the below listed cables including supply of single compression type brass glands, solder less crimping type copper sockets / lugs, Identification tags, Cu. clamp & wire for gland earthing etc.,
3.1 | XLPE Insulated & Steel Armoured Aluminium Conductor Cables
3.1.1 | 3.5C - 300 sq. mm AYFY | Each | 6 | 0 | 6
3.1.2 | 3.5C - 185 sq. mm AYFY | Each | 0 | 2 | 2
3.1.3 | 3.5C - 95 sq. mm AYFY | Each | 0 | 0 | 0
3.1.4 | 4C - 50 sq. mm AYFY | Each |  |  | 0
3.1.5 | 4C - 35 sq. mm AYFY | Each |  |  | 0
3.1.6 | 4C - 25 sq. mm AYFY | Each | 0 | 0 | 0
3.1.7 | 4C - 16 sq. mm | Each | 32 | 24 | 56
3.1.8 | 4C - 10 sq. mm | Each | 8 | 8 | 16
3.2 | PVC Insulated & Un Armoured Copper flexible Conductor cables (YY Type)
3.2.1 | 1C - 95 sq. mm | Each | 74 | 0 | 74
3.2.2 | 1C - 70 sq. mm | Each |  |  | 0
3.2.3 | 1C - 35 sq. mm | Each | 56 | 0 | 56
3.2.4 | 1C - 25 sq. mm | Each |  |  | 0
3.2.5 | 1C - 16 sq. mm | Each | 14 | 0 | 14
3.2.6 | 1C - 10 sq. mm | Each |  |  | 0
3.3 | PVC Insulated & Steel Armoured Copper Conductor cables (YFY Type)
3.3.1 | 4 Core - 120 Sq. mm YFY | Each | 0 | 2 | 2
3.3.2 | 4 Core - 25 Sq. mm YFY | Each |  |  | 0
3.3.3 | 4 Core - 16 Sq. mm YFY | Each | 28 | 28 | 56
3.3.4 | 4 Core - 10 Sq. mm YFY | Each | 0 | 0 | 0
3.3.5 | 4 Core - 6 Sq. mm | Each | 0 | 0 | 0
3.3.6 | 4 Core - 4 Sq. mm | Each | 0 | 0 | 0
3.3.7 | 3 Core - 6 Sq. mm | Each |  |  | 0
3.3.8 | 3 Core - 4 Sq. mm | Each | 8 | 8 | 16
3.3.9 | 3 Core - 2.5 Sq. mm | Each | 0 | 0 | 0
TOTAL FOR CABLES & ENDTERMINATION:
3 | MCB DISTRIBUTION BOARDS (DB)
Providing and Fixing of wall mounted MCB DBs with MS wire way box on top / bottom & on sides. MCBs shall be rated for 10kA with current limiting feature. Dummy ways to be covered with blank plates. All out going ways shall be labelled & laminated in as built drawing. Internal specifications to be considered as mentioned below for respective DBs'. All Enclosures will be IP-43
LDB & ELDB's :
3.1 | 10 Way TPN MCB DB | Each | 4 | 4 | 8
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TPN, MCB
Sub Incomer : 3Nos. 25A, DP, 30mA RCCB
Outgoing : 30 Nos. 10A SP MCB of 'C' curve
3.2 | 6 Way TPN MCB DB | Each | 0 | 0 | 0
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TPN, MCB
Sub Incomer : 3Nos. 25A, DP, 30mA RCCB
Outgoing : 18 Nos. 10A SP MCB of 'C' curve
RPDB :
3.3 | 10 Way TPN MCB DB | Each | 3 | 3 | 6
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TPN, MCB
Sub Incomer : 3Nos. 25A, DP, 100mA RCCB
Outgoing : 30 Nos. 16A SP MCB of 'C' curve
3.4 | 6 Way TPN MCB DB | Each |  |  | 0
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TPN, MCB
Sub Incomer : 3Nos. 25A, DP, 100mA RCCB
Outgoing : 18 Nos. 16A SP MCB of 'C' curve
UPSDBs' :
3.5 | 10 Way TPN MCB DB | Each | 5 | 5 | 10
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TPN, MCB - Curve D'
Sub Incomer : 6 Nos. 40A, DP, MCB - Curve D'
Outgoing : 24 Nos. 20A SP MCB of 'D' curve
3.6 | 6 Way TPN MCB DB | Each | 0 | 0 | 0
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TPN, MCB - Curve D'
Sub Incomer : 3 Nos. 40A, DP, MCB - Curve D'
Outgoing : 12 Nos. 10A SP MCB of 'D' curve
Main Emergency DB
3.7 | 12 Way VTPN MCCB DB | Each | 1 |  | 1
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 63A, TPN, MCCB
Outgoing : 12 Nos. 40A TP MCB - Curve C'
ELDB's & VAV DB's
3.8 | 8 Way ETPN MCB DB | Each | 4 | 4 | 8
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 40A, TP, MCB - Curve C'
Sub Incomer : 3Nos. 25A, DP, 30mA RCCB
Outgoing : 18 Nos. 10A SP MCB of 'C' curve
3.9 | Signage DB
| 4 Way SPN MCB DB (SPN Type ) | Each | 1 |  | 1
Enclosure : IP 42 Sheet steel with acrylic door
incomer : 1No. 25A, 2P, 300mA RCCB
1No. Programmable day timer & 32A Power Contactor
Outgoing : 4 Nos. 10/16A SP MCB of 'C' curve
Server / HUB DB's
3.1 | 8 Way TPN MCB DB | Each | 2 |  | 2
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 63A, TPN, MCB - Curve D'
Outgoing : 12 Nos. 32A DP MCB of 'D' curve
3.11 | 4 Way TPN MCB DB | Each | 2 | 4 | 6
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 63A, TPN, MCB - Curve D'
Outgoing : 6 Nos. 32A DP MCB of 'D' curve
Automation DB's
3.12 | 8 Way VTPN MCB DB | Each | 1 | 1 | 2
Enclosure : IP 43 Sheet steel
Incomer : 1Nos. 63A, TPN, MCB
Outgoing : 8 Nos. 40A TP MCB - Curve C'
TOTAL FOR DISTRIBUTION BOARDS:
4 | CIRCUIT / SUB MAINS:
Circuit mains using 1.1kV grade PVC FRLS insulated copper conductor wires / sheathed single core cables drawn in GI conduits. Rates quoted shall include supply of conduits, wires & other conduiting accessories.Circuit mains shall be measured from respective DB to the nearest control switch /socket board. Colour coding shall be used for conduits to differentiate lighting, RP, UPS, emergency lighting circuits & point wiring. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / socket outlets.
4.1 | Lighting Circuit:
4.1.1 | To wiring using (3R x 2.5) sqmm pvc insulated FRLS wire drawn in 20/25mm dia GI conduit as lighting circuit, being recond from the distribution board to first light control switch. (Looping will not be paid separately for next primary point) | Mtrs | 3450 | 3450 | 6900
4.1.2 | To wiring using (3R x 1.5) sqmm pvc insulated FRLS wire drawn in 20/25mm dia GI conduit as lighting circuit, being recond from the distribution board to first light control switch. (Looping will not be paid separately for next primary point) | Mtrs | 1200 | 1200 | 2400
4.2 | UPS / RP Circuit:
4.2.1 | Supply & Installation of 3C x 2.5 Sqmm FR 1100V unarmoured double insulated flexible multicore cable in white and black colour for Equipment power: UPSDB/ RPDB circuit in exisitng raceways/ conduits/ wireways respectively. (6/ 8 workstation to be looped together for UPS power and 10 /12 workstation to be looped together for RAW power) | Mtrs | 7750 | 8450 | 16200
4.2.2 | Supply & Installation of 3C x 4 Sqmm FR 1100V unarmoured double insulated flexible multicore cable in white and black colour for Equipment power: UPSDB/ RPDB circuit in exisitng raceways/ conduits/ wireways respectively. (6/ 8 workstation to be looped together) | Mtrs |  |  | 0
4.3 | UPS Circuit (SERVER/ HUB room):
4.3.1 | Supply & Installation of 3C x 4 Sqmm FR 1100V unarmoured double insulated flexible multicore cable in white and black colour for UPS circuit in existing raceways/ conduits/ wireways. | Mtrs | 155 | 120 | 275
4.4 | Misc. Power & Kitchen Circuit:
4.4.1 | Supply & Installation of 3R x 4.0 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in 20/ 25mm GI conduit | Mtrs | 100 | 100 | 200
4.4.2 | Supply & Installation of 5R x 2.5 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in 20/ 25mm GI conduit | Mtrs | 30 | 30 | 60
4.4.3 | Supply & Installation of 5R x 4.0 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in 20/ 25mm GI conduit | Mtrs |  |  | 0
4.5 | For DB & SMSB Body / Clean Earthing
4.5.1 | 2 x 4 sqmm copper conductor wires in 19mm dia. conduit. | Mtrs | 40 | 40 | 80
4.5.2 | 2 x 6 sqmm copper conductor wires in 25mm dia. conduit. | Mtrs | 240 | 250 | 490
4.5.3 | 2 x 10 sqmm copper conductor wires in 25mm dia. conduit. | Mtrs | 150 | 150 | 300
4.5.4 | 1R x 4.0Sqmm copper conductor cable in existing raceway / conduit. | Mtrs | 200 | 200 | 400
( For false floor supports & rack body earthing )
TOTAL FOR CIRCUIT/ SUB MAINS:
5 | POWER RECEPTACLES.
Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions.
Note: Safety shutters to prevent accidental contact with live parts shall be provided. No indicator shall be provided for switches
5.1 | Modular Switch and Socket
5.1.1 | 1x 6A universal socket controlled by 10A SP switch | Nos. | 85 | 75 | 160
5.1.2 | 2x 6A universal socket controlled by 10A SP switch | Nos. |  |  | 0
5.1.3 | 3x 6A universal socket controlled by 16A SP switch | Nos. |  |  | 0
5.1.4 | 1x 13A International socket controlled by 10A SP switch | Nos. | 321 | 323 | 644
5.1.5 | 2x 13A International socket controlled by 10A SP switch | Nos. | 177 | 110 | 287
5.1.6 | 3x 13A International socket controlled by 16A SP switch | Nos. | 90 | 48 | 138
5.1.7 | 4x 13A International socket controlled by 16A SP switch | Nos. | 469 | 544 | 1013
5.1.8 | 1x 6/16A universal socket controlled by 16A SP switch | Nos. | 388 | 312 | 700
5.1.9 | 2x 6/16A universal socket controlled by 16A SP switch | Nos. | 10 | 10 | 20
5.1.10 | 1x USB port charger - Modular type | Nos. | 40 | 40 | 80
5:01 | 2x USB port charger - Modular type | Nos. |  |  | 0
5.2 | Server / Hub room Rack Sockets
5.2.1 | 1No. 6/16 A universal socket outlet controled by 6/16 A SP switch + 1No. 32A 3 pin 1phase Industrial type locakable socket with plug top controlled by 32A SP MCB enclosed in metal box. | Each | 28 | 20 | 48
5.3 | Industrial Sockets
5.3.1 | 20/32A 3pin 1phase Industrial socket with plug top controlled by 20/32A SP MCB enclosed in sheet metal box with necessary accessories complete as required. | Nos |  |  | 0
5.3.2 | 20/32A 3pin 1phase Industrial socket with plug top controlled by 20/32A DP MCB enclosed in sheet metal box with necessary accessories complete as required. | Nos | 2 | 2 | 4
5.3.3 | 20/32A 5pin 3phase Industrial socket with plug top controlled by 20/32A FP MCB enclosed in sheet metal box with necessary accessories complete as required. | Nos | 2 | 2 | 4
5.3.4 | 40/63A 5pin 3phase Industrial socket with plug top controlled by 20/32A FP MCB enclosed in sheet metal box with necessary accessories complete as required. | Nos |  |  | 0
5.3.5 | Floor box with 4 nos. of 13A scoket controlled by 2 no. 16A switch and 4 nos. of data port. (Make: Mk or equivalent fabricated.) | Nos | 40 | 50 | 90
5.4 | DP/ FP MCB Tye Isolators in MS Enclosure
5.4.1 | 40/ 63A, DP ELMCB in IP 42 MS Enclosure. | Nos | 4 | 6 | 10
5.4.2 | 40/ 63A, TPN ELMCB in IP 42 MS Enclosure. | Nos | 10 | 6 | 16
5.4.3 | 40/ 63A, DP MCB in IP 42 MS Enclosure. | Nos |  |  | 0
5.4.4 | 40/ 63A, TPN MCB in IP 42 MS Enclosure. | Nos |  |  | 0
TOTAL FOR POWER RECEPTACLES:
6 | POINT WIRING
Supply, Installation, Testing & Commissioing of Wiring of light points, fan points, 6A socket outlets using GI conduit of 19/25 mm dia with accessories, using 3 runs of 1.5 Sqmm 1100v grade PVC FRLS insulated copper wires, modular switches with MS box, plate & accessories. point drops shall be by flexible conduit. The cost of circuit to be measured seperately.
6.1 | PRIMARY LIGHT POINT: | Nos. | 200 | 155 | 355
Primary light point means wiring from first switch control to the first light point outlet. Cost of switch, face plate & back boxes etc. to be considered.
Not to include the incoming lighting circuit from MCB - DB to switch boards and looping from switch boards to switchboards.
For drops from the ceiling flexible conduit shall be included, with gland on both sides
6.2 | POINT WIRING - MCB Control | Nos. | 275 | 225 | 500
Primary light point means wiring from MCB control in DB to the first light point.
For drops from the ceiling flexible conduit shall be included, with gland on both sides
6.3 | SECONDARY LIGHT POINT: | Nos. | 420 | 390 | 810
Secondary light point means extention of light outlet point from adjascent light points existing.
For drops from the ceiling flexible conduit shall be included, with gland on both sides
TOTAL FOR POINT WIRING:
7 | LIGHT FIXTURES:
Provide, Installation, Testing and Commissioning of lights fixtures LED/ Decorative type. The cost of fixtures to be consfdered with all accessiores,suspensions, fixing arrangements etc.
7.1 | 32 W Recess Mounted LED Luminaire, 600mm x 600mm to be fixed in grid ceiling, | Nos. | 310 | 385 | 695
7.2 | Recessed downlight, 15 W LED panel lights installed in cabins and enclosed places | Nos. | 100 | 42 | 142
7.3 | Recessed, 15 W COB LED fixtures with black finish to be installed in passages | Nos. | 210 | 180 | 390
7.4 | Recessed, 10 W COB LED to be installed as wall washers | Nos. | 54 | 20 | 74
7.5 | Suspended type downlight with 12/15 W LED. | Nos. | 22 | 0 | 22
7.6 | Linear Light Fixtures
7.6.1 | 4 feet long, 26/28 W LED linear luminaire suspended from ceiling, Light supliers to provide the suspensions. | Nos. | 26 | 24 | 50
7.6.2 | 6 feet long, 26/28 W LED linear luminaire suspended from ceiling, Light supliers to provide the suspensions. |  | 36 | 20 | 56
7.6.3 | 8 feet long, 52/56 W LED linear luminaire suspended from ceiling, Light supliers to provide the suspensions. | Nos. | 40 | 10 | 50
7.7 | 4 feet long, 28 W T5 LED Fitting fixed either on ceiling or suspended from ceiling | Nos. | 15 | 15 | 30
7.8 | 14.5 W/ Mtr. LED stip lights with drivers, drivers ratings to be selected as per the length available at site. If required multiple drivers to serve the purpose. A Length of 5 mtrs to be considered as a single unit | Mts | 20 | 18 | 38
7.9 | Decorative type light fixtures as selected and approved by Architect/ Interior Designer for asthetic look and feel. These light fixtures may be installed at places as deciided by them. Basic cost mentioned below stands to the complete fixtures, suspension and fixing arrangemnets etc). In case there would be a price variation apart from these below mentioned prices as landing cost a detailed break up to be submitted and will be considered as an additional item
7.9.1 | Decorative type Light fixture as selected and approved by architect - (Landed cost: 4500/-). | Nos. | 4 | 4 | 8
7.9.2 | Decorative type Light fixture as selected and approved by architect - (Landed Cost: 8500/-). | Nos. | 2 | 2 | 4
7.9.3 | Decorative Light fixture as approved by architect - (Landed Cost: 12000/-). | Nos. | 2 | 2 | 4
7.9.4 | DecorativeLight fixture as approved by architect - (Landed Cost: 15000/-). | Nos. | 0 | 0 | 0
7.9.5 | Outdoor lighting (basic cost to be considered is 8000/-) | Nos. | 0 | 0 | 0
7.9.6 | Bollard lighting/ Wall lights for terreace area (basic cost to be considered is 4500/-) | Nos. | 4 | 4 | 8
7.1 | Provide, Installation, Testing and Commissioning of motion/ occupancy cum day light sensor PIR sensors to be installed in cabins and enclosed spaces as required with a covering area of 6-6.5 meters in diameter when installed at a height of 2700mm | Nos. | 40 | 40 | 80
7.11 | Provide, Instalaltion, Testing & Commissioning of Dali ballast (0-10 Volts) for dimming at places where audio-video is considered | Nos. | 115 | 75 | 190
7.12 | Provide, Installation, Testing & Commissioning of 230 volts, 50 Hz buzzer for handicapp toilet. | Nos. | 1 | 1 | 2
TOTAL FOR LIGHT FIXTURES:
8 | CABLE TRAYS
GI ready made cable trays. Quoted rates for installation shall include necessary anchor fasteners / 'L' angle supports @ 600mm interval etc., to suit site conditions
8.1 | LADDER TYPE :
8.1.1 | 300 x 50mm Size (2.0 mm Thk.) | Mtrs | 250 | 250 | 500
8.1.2 | 200 x 50mm Size (2.0 mm Thk.) | Mtrs |  |  | 0
8.1.3 | 150 x 50mm Size (2.0 mm Thk.) | Mtrs |  |  | 0
8.2 | PERFORATED TYPE :
8.2.1 | 450 x 75mm Size (2.0 mm Thk.) | Mtrs |  |  | 0
8.2.2 | 300 x 50mm Size (2.0 mm Thk.) | Mtrs | 180 | 180 | 360
8.2.3 | 200 x 50mm Size (2.0 mm Thk.) | Mtrs | 75 | 75 | 150
8.2.4 | 150 x 50mm Size (2.0 mm Thk.) | Mtrs | 50 | 50 | 100
TOTAL FOR CABLE TRAYS:
9 | GI RACEWAYS & JUNCTION BOXES:
9.1 | GI Junction boxes with cover. Junction Boxes shall have cutouts for mounting socket outlets. Dimensions mentioned below are the inner clearence. Rate shall include necessary anchor fastener mounting / fixing arrangements
9.1.1 | 450 x 450 x 60mm Size (2.0 mm Thk.) | Nos. | 12 | 12 | 24
9.1.2 | 350 x 350 x 60mm Size (2.0 mm Thk.) | Nos. | 75 | 90 | 165
9.1.3 | 300 x 300 x 60mm Size (2.0 mm Thk.) | Nos. | 70 | 80 | 150
9.1.4 | 250 x 250 x 60mm Size (2.0 mm Thk.) | Nos. |  |  | 0
9.1.5 | 150 x 150 x 60mm Size (1.6 mm Thk.) | Nos. | 275 | 235 | 510
9.2 | Raceways mounted below false floor / above false ceiling / inside cladding or on wall. Rate shall include necessary anchor fastener mounting / fixing arrangement
GI Raceways
9.2.1 | 100x40mm Size (1.6 mm Thk.) | Mtrs | 1550 | 1650 | 3200
9.2.2 | 200x40mm Size (1.6 mm Thk.) | Mtrs | 120 | 165 | 285
9.2.3 | 300x40mm Size (1.6 mm Thk.) | Mtrs | 250 | 250 | 500
9.2.4 | 450x75mm Size (2.0 mm Thk.) | Mtrs | 10 | 10 | 20
Powder coated Raceways
9.3 | Raceways mounted below false floor / above false ceiling / inside cladding or on wall. Rate shall include necessary anchor fastener mounting / fixing arrangement
9.3.1 | 100x40mm Size (2.0 mm Thk.) | Mtrs | 30 | 25 | 55
9.3.2 | 200x40mm Size (2.0 mm Thk.) | Mtrs |  |  | 0
9.3.3 | 300x40mm Size (2.0 mm Thk.) | Mtrs |  |  | 0
9.3.4 | 450x100mm Size (2.0 mm Thk.) | Mtrs | 25 | 25 | 50
9.4 | Supply & Laying of following size GI conduits.
9.4.1 | 32mm dia | Mtrs |  |  | 0
9.4.2 | 25mm dia | Mtrs | 800 | 800 | 1600
9.4.3 | 20mm dia | Mtrs | 300 | 300 | 600
9.5 | Floor cutting, chipping and removal of debris for the above raceways | Mtrs | 1550 | 1650 | 3200
TOTAL FOR RACEWAYS:
10 | EARTHING
10.1 | Maintenance Free Earth pits Eathing system shall be installed as per supplier guidelines /details. Rate shall include necessary civil works
Make : ASHLOK/ FAST TRACK or Equ.
10.1.1 | Type-1 : Single Rod configuration | Each. | 10 |  | 10
10.2 | EARTH STRIPS
GI/Cu earth strips on cable tray or below ground as per site condition. All Cu. Strips shall be run in pvc heat shirnkable sleeve & mounted on insulation mounts. Cost of civil works shall be included for strips laid below ground. All main GI earth strips
10.2.1 | 8 SWG GI Wire | Mtrs | 100 | 100 | 200
10.2.2 | 25 x 3mm GI Earth flat | Mtrs | 180 | 180 | 360
10.2.3 | 25 x 6mm GI Earth flat | Mtrs | 353 | 353 | 706
10.2.4 | 50 x 6mm GI Earth flat | Mtrs | 120 | 120 | 240
10.2.2 | 25 x 3mm Cu. Earth flat | Mtrs | 25 | 18 | 43
10.3 | Bus-bar terminals
10.3.1 | Busbar of 0.5 Mtr length made out of 50x6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | Nos | 6 | 6 | 12
10.3.2 | Busbar of 0.5 Mtr length made out of 25x6 mm Cu. Strip with drill holes of M8 at 25mm interval mounted on insulators. | Nos | 6 | 6 | 12
10.4 | PVC Insulated & Unarmoured Copper flexible Conductor cables (YY Type)
1.1kV grade, copper conductor, PVC insulated, unarmoured, power cables. The cables shall be laid on tray / hume pipe /in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. Rate quoted shall exclude cost of tray / hume pipe
10.4.1 | 1C - 120 sq. mm | Mtrs | 0 | 0 | 0
10.4.2 | 1C - 95 sq. mm | Mtrs | 545 | 0 | 545
10.4.3 | 1C - 50 sq. mm | Mtrs | 90 | 0 | 90
10.4.4 | 1C - 25 sq. mm | Mtrs | 360 | 206 | 566
10.4.5 | 1C - 16 sq. mm | Mtrs | 170 | 10 | 180
10.4.6 | 1C - 10 sq. mm | Mtrs | 570 | 270 | 840
10.5 | End terminations for the below listed cables including supply of single compression type brass glands, solder less crimping type copper sockets / lugs, Identification tags, Cu. clamp & wire for gland earthing etc.,
10.5.1 | 1C - 120 sq. mm | Nos |  |  | 0
10.5.2 | 1C - 95 sq. mm | Nos | 4 |  | 4
10.5.3 | 1C - 50 sq. mm | Nos | 14 | 6 | 20
10.5.4 | 1C - 25 sq. mm | Nos | 10 | 10 | 20
10.5.5 | 1C - 16 sq. mm | Nos | 22 | 20 | 42
10.5.6 | 1C - 10 sq. mm | Nos | 8 |  | 8
TOTAL FOR EARTHING:
11 | MISCELLANEOUS ITEMS
11.1 | RCC Hume pipe ( For road crossing ) of following size 300- 500mm below ground level, inclding collars & civil works.
11.1.1 | 200mm dia | Mtrs |  |  | 0
11.1.2 | 300mm dia | Mtrs | 20 |  | 20
11.2 | Safety / Statutory requirements
11.2.1 | 6mm thick rubber mat of 1.1KV class and 1000mm wide | Nos. | 10 | 0 | 10
11.2.2 | Shock treatment chart as approved by the Electrical Inspectorate mounted on teak wood frame and suitable for wall mounting. - Both English and Local Language | Nos. | 1 | 1 | 2
11.2.3 | First aid kit with certification | Nos. | 1 | 1 | 2
11.3 | Earth Pits Boards | Nos. | 0 | 0 | 0
11.4 | MS Fabricated Items | Kg. | 20 | 20 | 40
11.5 | HDMI Cables 5 to 10 Mtrs | Nos | 0 | 0 | 0
11.5 | VGA Cables 10 to 15 Mtr | Nos | 0 | 0 | 0
11.5 | Professional Charges:
| Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electrical. | Each | 1 | 1 | 2
11.6 | Temperory Lighting
| Temporary Lighting & Power arrangement with sufficient temporary Lighting (Min 30 Lux Avg.) & power shall be provided to all agencies at 4 different locations and further the respective agencies has to tap as per their requirement. | Ls. | 1 | 1 | 2
TOTAL FOR MISC:
SUMMARY
LT Panels:
LT Cables and Endtermination:
MCB Distribution boards:
Circuit and Submains:
Power Receptacle:
Point wiring:
Ligth fixtures:
Cable Trays:
Raceways:
Earthing:
Misc Items:
Total for Electrical & Associated Works:
| Add Central GST @9% | [6 empty] | 0 | 0
| Add State GST @9% | [6 empty] | 0 | 0
| Total: | [6 empty] | 0 | 0
| Grand Total: | [7 empty] | 0
Note:
1 | Toilet area is not considered in scope of work, Circuit will be provided from the floor DB. Emergency Light points will be provided
2 | All the conduits considered are GI as instructed by the base developer
3 | Dimmable ballast for AV is consiedred in this boq.
4 | Floor-pop up boxes are consiedred.
5 | We have not considered the emergency UPS cost in the BoQ, the same will be shared separately along with the other requirements of UPS.

## CONSIDER MAKE
MEP List Of Makes
Sr. | Description | Makes
I | Electrical & Associated Works
1 | Power Panel manufacturer | Powercon
2 | MCB/ MPCB/ RCCB/ RCBO: | Hager
3 | MCB Distribution Boards: | Hager
4 | HT/ LT Armored cables: | KEI
5 | Single Core Cu. Flex. Cables: | KEI
6 | LT Multi Core Cu. Flex. Cables: | KEI
7 | PVC Insulated Copper Wires: | KEI
8 | Lugs for Cable End termination: | Dowells
9 | Glands for Cable termination: | Cosmos
10 | Accessories for PVC Conduits: | Precision
11 | PVC Conduits: | Precision
12 | GI /MS conduit and accessories: | BEC Conduits Pvt. Ltd./ AKG
13 | Cable trays, Trunking and Raceways: | Locally Fabricated
14 | Modular type Power Receptacles: | Crabtree - Signia
15 | Industrial Metal Clad Sockets: | Neptune/ Scame
16 | Floor Box | MK / Equ.